## Sheet1
Quality Assurance Plan : Chiller Unit Assembly |  |  |  |  | Document No : QAP/STD/300, Rev: 00 |  |  |  |  | Page 1 of 2
Sr. No | Item Description | Check |  |  | Acceptance Norms | Format Of Record | Inspection By |  |  | Remarks
|  | Characteristics | Method | Extent |  |  | M | C | I
1 | Compressor Assembly
1a | Compressor Assembly | Pressure Test | Certificate Review | 100% | Manufacturer Specification | Manufacturer Certificate | R/P | R | R
1b | Motor for compressor | Motor Insulation test | Meager | 100% | KCPL Specification | Inspection Report | P | R | R
2-A | Heat Exchanger Assembly (Evaporator for all Chillers & Condenser for Water Cooled Chiller Models)
2a | Pneu. Test: Ref. Side | Leakage/ Pr. drop | Visual | 100% | No any leakage and/ or pressure drop | Insp. Report | P | R | R
| Hydro Test: Water side | Leakage/ Pr. drop | Visual | 100% |  | Insp. Report | P | R | R
2-B | Condenser Coils (For air cooled chiller models)
2a | Pressure testing | Leakage/ Pr. Drop | Visual | 100% | Drawing, Material specification. | Inspection Report | P | R | R
3 | Panel Inspection
3a | Panel Inspection | Visual, dimensions | Visual Measurement | 100% | KCPL drgs / specification | Insp. Report | P | R | R
|  | Component Layout |  |  |  |  | P | R | R
|  | Wiring check |  |  |  |  | P | R | R
4 | Chiller Unit Assembly
4a | Pneumatic Pressure Test (Refrigerant side) | Leakage/ Pr. Drop | Visual | 100% | No any leakage and/ or pressure drop | Insp. Report | P | R | R
4b | Performance Testing | Performance | Run Test. | Ask per remark | KCPL Specification | Log Sheet | P | R | R | Performance run test of chilers shall be carried out at design & 100% load codition
4c | Final Inspection | Finish Painting | Visual & DFT | 100% | KCPL Specification | Insp. Report | P | R | R
|  | Insulation | Visual | 100%
|  | Name plate, labels | Visual | 100%
Quality Assurance Plan : Chiller Unit Assembly |  |  |  |  | Document No : QAP/STD/300, Rev: 00 |  |  |  |  | Page 1 of 2
Legends Used:
M
C
I
P
H
R
NA
Abbreviations:
KCPL
MTC
Checked & Approved By : DVD
5.4.14
QA Plan Prepared By : RVH
DVD (QA)
REV | Revision Description |  |  | Date | Approved By |  |  | 5.4.14 |  | Accepted By